Dallas Parkway 12 Inch Water Line

December 7, 2012

RE:	Plan Review Comments

After reviewing the plans provided at the pre-construction meeting, Addison Public Works has the following comments:

Sheet 1 of 3:  	STA 0+03 – New 12 inch tap; abandon 8 inch altogether.  Will need 36 x 12 tap sleeve and valve, 12” 45 bend,

2 - 12” 90 bends, sufficient 12 inch pipe to get to DP alignment.

STA 0+41 – This is apparently a 6” stub-out for no current purpose other than a 2 inch irrigation service.  Upsize to 8 inch for future development.

STA 0+45 – New 2 inch tap for irrigation service (tap 12” or 6/8” ?)

STA 2+29 – Salvage or relocate/re-use hydrant?  Exist. 8” plug (N&S).

STA 2+46 – Remove exist. 8” valve; add 12” valve; new 8” valve on T; Plug exist. 8” (N&S).

STA 2+56 – New 2 “ tap for irrigation service.

STA 4+78 – Remove exist. 8” valves (2)

Sheet 2 of 3:	STA 5+99 – Add 12” valve

STA 9+80 – Add 2” tap for irrigation service

STA 9+87 – Add 12” valve; Is there room between the new 6” valve and the existing hydrant location?  The hydrant may need to be moved back from the curb a little further.  (Field decision)

  - ~STA 5+45 – show ex. 6” wastewater line in profile & encase proposed water line if 2’ clearance is not possible.

  - ~STA 5+70 – encase proposed water line if 2’ clearance is not possible between water and storm.

  - ~STA 8+65 – revise water line profile to allow 2’ clearance between water and storm, or encase proposed water line if 2’ clearance is not possible.

Sheet 3 of 3:	STA 13+17 – Add 12” valve

STA 13+17 – Add 2” tap for irrigation service

STA 14+63 – Plug 12” water (W)

  - ~STA 11+33 – proposed water line encasement shown on DWU line, not Addison line in the plan view.

  - ~STA 13+17 & 13+21 – callouts in plan view do not match call-outs in profile view.

Points of Discussion:

- General

  - Coordinate end of line connection points and alignments with Town of Addison Public Works prior to beginning construction

  - Please locate valves at tees on south side of tees rather than north side.

  - Phasing and Testing

- Sheet 1 of 3

  - Upsize tee and stub-out at 0+41 to an 8” line for future use.

- Sheet 2 of 3

  - ~STA 5+45 – show ex. 6” wastewater line in profile & encase proposed water line if 2’ clearance is not possible.

  - ~STA 5+70 – encase proposed water line if 2’ clearance is not possible between water and storm.

  - ~STA 8+65 – revise water line profile to allow 2’ clearance between water and storm, or encase proposed water line if 2’ clearance is not possible.

- Sheet 3 of 3

  - ~STA 11+33 – proposed water line encasement shown on DWU line, not Addison line in the plan view.

  - ~STA 13+17 & 13+21 – callouts in plan view do not match call-outs in profile view.