STREET LIGHTING & CONDUIT NOTES

1.  REFER TO SHEET 3 "GENERAL CONSTRUCTION NOTES, LEGEND AND ABBREVIATIONS" FOR THE GENERAL CONSTRUCTION NOTES FOR THE PROJECT.

2.  REFER TO SHEET ED (1)-03 FOR ELECTRIC DETAILS - CONDUIT.  RIGID METAL CONDUIT ELBOWS ARE NOT REQUIRED.

3.  REFER TO SHEET ED (2)-03 FOR ELECTRIC DETAILS - CONDUCTORS.

4.  REFER TO SHEET ED (3)-03 FOR ELECTRIC DETAILS - GROUND BOXES.  RIGID METAL CONDUIT ELBOWS ARE NOT REQUIRED.  CONCRETE APRON IS NOT REQUIRED.

5.  REFER TO SHEET ED (5)-03 FOR ELECTRIC DETAILS - SERVICE ENCLOSURE & NOTES, ELECTRICAL SERVICE TYPE D.

6.  REFER TO SHEET ED (8)-03 FOR ELECTRIC DETAILS - ELECTRICAL SERVICE SUPPORT PEDESTAL SERVICE TYPE PS.  PEDESTAL SERVICE SHALL BE ALUMINUM, COLOR PINE GREEN.  RIGID METAL ELBOWS ARE NOT REQUIRED.

7.  WATER, SANITARY SEWER, AND STORM DRAIN LINES ARE SHOWN FOR REFERENCE ONLY.  CONTRACTOR SHALL LOCATE ALL UTILITY LINES IN THE AREA PRIOR TO DIGGING.

8.  INSTALL SCHEDULE 40 PVC UNDERGROUND (24" MIN COVER) .  ALL STREET AND DRIVEWAY CROSSINGS (30" MIN COVER).  ALL BENDS TO LONG RADIUS.

9.  ALL CONDUIT AT POLE BASES TO BE WITHIN THE DRILLED SHAFT FOUNDATION.  NO EXPOSED CONDUIT AT POLE BASES WILL BE ALLOWED

10.  SL TYPE 1  -  SINGLE 100W 240V MH LUMINARE ON 11'-8" POLE,

COLOR SILVER- REFERENCE SPECIAL PROVISIONS

SL TYPE 2  -  TWIN 100W 240V MH LUMINARE ON 11'-8" POLE,

COLOR SILVER- REFERENCE SPECIAL PROVISIONS

SL TYPE 3 -   SINGLE 400 W 240V MH LUMINARE ON 30' POLE,

COLOR SILVER- REFERENCE SPECIAL PROVISIONS

SL TYPE 4 - TWIN 400 W 240V MH LUMINARE ON 30' POLE,

COLOR SILVER- REFERENCE SPECIAL PROVISIONS

11.  CONNECTION TO POWER COMPANY CIRCUITS TO BE MADE ONLY BY POWER COMPANY.

12.  UNLESS OTHERWISE INDICATED ALL WORK SHALL CONFORM TO THE 2008 NATIONAL ELECTRICAL CODE (NFPA 70) AND THE 2007 NATIONAL ELECTRICAL SAFETY CODE (ANSI C2).

13.   ALL EMPTY CONDUIT INSTALLED FOR FUTURE EXTENSION SHALL BE TURNED UP AND EXTENDED UP TO FINISHED GRADE.  CAP ENDS OF ALL CONDUITS.

14.  REFER TO REFERENCED SHEETS FOR STREET LIGHTING DETAILS.

15.  IRRIGATION SLEEVES "IRR" SHALL CONSIST OF 1-6" SCH 40 PVC AND 1-2" SCH 40 PVC INSTALLED WITH MINIMUM 24" COVER AND EXTENDING 2' BEYOND THE BACKS OF CURB OR EDGE OF PAVEMENT AND UP TO FINISHED GRADE.  CAP ENDS OF ALL CONDUITS.