WATER & SANITARY SEWER CONSTRUCTION NOTES:

- All materials, construction, testing and workmanship shall conform to the Town of Addison Standard Construction Details and Specifications for Public Works Construction.

- All Water Mains 6" and larger will be C900 DR14 Polyvinyl Chloride.

- Water mains eight inches (8”) to twenty-four inches (24”) in diameter shall be AWWA C905 / DR18 PVC, mechanical joint or a joint of the type which provides a recession in the bell for the employment of a single rubber gasket to be placed before the insertion of the succeeding spigot. Joint material for PVC shall Conform to ASTM F477.

- All water Line pipe shall be imbedded per Town of Addison standards.

- MINIMUM COVER:

PIPE DIAMETER              COVER		PIPE DIAMETER              COVER

# Less Than 6"                     42"		8"                                       48"

6"                                       42"		Greater than 8"                  54-60"

- All water lines shall have a 150 psi Hydrostatic test for a four hour period. Test shall be witnessed by the Engineering Inspector. All Fire mains shall have a 200 psi Hydrostatic test for a two hour period.

- All water mains must be chlorinated by the contractor and water samples then must be taken and provided to the Town of Addison.

- All water line valves, main line taps, fittings and fire hydrants shall be placed in a concrete saddle and thrust blocks.

- All valve boxes shall be adjustable Cast Iron type and shall be placed on a concrete base. A reinforced concrete pad of 3'-0"x3'-0"x6" shall be poured around the valve box in areas outside of the pavement.

- Fire hydrants shall be placed to conform with the requirements of the State Board of Insurance and Fire Prevention and Engineering Bureau of Texas. The fire hydrant shall be set perpendicular, and to the proper depth, and shall be carefully and substantially blocked against firm trench walls using 2000 psi concrete.

- Sanitary sewer mains shall be polyvinyl chloride pipe conforming to the specifications of ASTM D 3034, SDR 35, or equal. Joints and fittings shall be compression rubber gasket joints.

- Sanitary sewer pipe shall be placed on a 4" layer of crushed stone. The trench shall be back filled per Town of Addison standards and consolidated to a minimum of 90% standard proctor density.

- Testing for sanitary sewer system shall be per the North Central Texas Council of Governments Standard Specifications.

- All water and sanitary sewer service locations shall be marked on the nearest curb face with a "W" & "S" respectively.

- All plumbing installed outside of R.O.W. or and Easement shall be installed by a Licensed Plumber and inspected by Building Inspection.

- Fire sprinkler line shall be sized and installed by a State Licensed Contractor.

- The Contractor shall tie detectable green metallic tape to the end of sewer service or buried dead end and shall leave a minimum of 36" of tape exposed after backfill is complete.

- The Contractor shall be responsible for providing "As-Built" plans to the design engineer of record showing the location of water & sanitary sewer services.

- Contractor shall have a Trench Safety Plan.

- See Town of Addison Standard Construction Details for Additional General Notes.