Scope of work related to the Addison Athletic Club

BASE BID

1.0 CARDIO WING

Demolition Scope:

Provide all labor, tools, equipment, materials, disposal, installation and all things necessary to accomplish the following, per TOA specification:

1.01	Remove five (5) package A/C units, condensate drain, duct heaters, t-stats and all associated ductwork within the mechanical room on the ground floor. Remove all associated disconnect switches and electrical connections.

1.02	Remove any landscaping and/or trees on site where the new 200 ton chiller and associated pumps will be located. Prepare site for the new concrete housekeeping pad.

1.03	Remove all existing supply grilles serving cardio space on the second floor.

1.04	Remove all circle grid located below the lights on the second floor.

New scope:

Provide all labor, tools, equipment, materials, disposal, installation and all things necessary to accomplish the following, per TOA specification:

1.05	Provide a new packaged 200 ton air cooled chiller, associated inline chiller pumps, and 6” housekeeping pad.

1.06	Provide six (6) new air handling units, associated supply/return ductwork, condensate drains, 1-1/4” CHS/R piping and electric duct heaters within the existing mechanical room on the ground floor. Provide new DCC controls and t-stats. Provide new 30/3/15 disconnect switch and reconnect to the existing panel.

1.07	Provide one (1) new air handling unit suspended from the structure, associated CHS/R piping connections, and thermostats to serve the staff area. Provide new 30/3/15 disconnect switch and reconnect to the existing panel.

1.08	Provide six (6) new chilled water cassettes within the cardio space on the second floor. Extend chilled water lines from mechanical room below to the new cassette. Route new condensate drains lines to the existing floor drains within the existing mechanical room on the ground floor. Provide new 2P15A circuit breakers and conduit for the existing electrical panel.

1.09	Provide new 6” insulated CHS/R piping from the chiller routed to the ground floor to the new six (6) new AHU. The new 6” CHS/R shall extend to the existing mechanical room in the original building and tie into the existing CHS/R piping.

1.1	Provide new supply diffusers to replace the existing supply grilles that were removed within the demolition scope.

1.11	Provide six (6) new high volume low speed fans in the middle of each cardio bay on the second floor.  Provide new 2P25A circuit breakers from the existing electrical panel, conduit and motor thermal overload switch. Provide one recessed lockable panel for the main control panel operating the fans.

1.12	Repair gyp/lay in ceiling and walls damaged by the ceiling cassettes and construction.  Match adjacent finishes and color. Paint the walls and ceiling in its entirety surface to avoid color matching issues.

1.13	Provide 30 days continuous data logger on the two existing electrical service disconnect switches to record KW and peak KW.

BASE BID

2.0 ORIGINAL BUILDING

Demolition Scope:

Provide all labor, tools, equipment, materials, disposal, installation and all things necessary to accomplish the following, per TOA specification:

2.01	Remove four (4) air handling units and associated pneumatic thermostat located within the existing mechanical room or above the existing lay in ceiling. Disconnect the existing electrical connection, supply ductwork, and return ductwork for reconnection to the new air handling unit.

2.02	Disconnect the electrical connection and lock the circuit breakers to the existing chiller, cooling tower and associated pumps. Equipment shall be taken out of service.

New scope:

2.03	Provide all labor, tools, equipment, materials, disposal, installation and all things necessary to accomplish the following, per TOA specification:

2.04	Provide four (4) new air handling units and reconnect the supply ductwork, return ductwork, and electrical connections. Provide new DCC controls and t-stats.

2.05	Repair gyp/lay in ceiling and walls damaged by the air handling unit installation.  Match adjacent finishes and color. Paint the walls and ceiling in its entirety surface to avoid color matching issues.

ALTERNATE BIDS

3.0 ORIGINAL BUILDING

Demolition Scope:

Provide all labor, tools, equipment, materials, disposal, installation and all things necessary to accomplish the following:

3.01	Remove five (5) air handling units and associated pneumatic thermostat located within the existing mechanical room or above the existing lay in ceiling. Disconnect the existing electrical connection, supply ductwork, and return ductwork for reconnection to the new air handling unit.  Provide new DCC controls and t-stats.

3.02	Remove the existing ductwork and supply grilles serving the gymnasium.

New scope:

Provide all labor, tools, equipment, materials, disposal, installation and all things necessary to accomplish the following:

3.03	Provide five (5) new air handling unit and reconnect the supply ductwork, return ductwork, and electrical connections.

3.04	Provide new fabric duct and cabling system serving the gymnasium.

3.05	Replace the existing roof mounted relief air hood within the gymnasium and install a motorized damper at the roof opening to modulate as required to maintain the building pressurization.

3.06	Repair gyp/lay in ceiling and walls damaged by the air handling unit installation.  Match adjacent finishes and color. Paint the walls and ceiling in its entirety surface to avoid color matching issues.

3.07	Provide a new 480V/3 phase electrical service with a 1200 amp switchboard to serve the new chiller and duct heaters.