## Sheet1
Town of Addison
Summary of Engineering Review Comments
Date: | 2019-08-23 |  | Town Project #:19-09D
Plan Review : | Civil Review 1
Received: | 2019-07-30 |  | Prepared by: JP
Plan Date: | 2019-07-25
Development: | Galaxy FBO
All comments on Plan Review Set and Summary of Review Comment form must be addressed. Summary of Review Comment form may NOT be all inclusive of comments made directly on the Plan Review Set.
Page No. | Comments | Response (See Note) | Explanation
GENERAL | Incorporate changes requested from most recent zoning review. | AGREE
GENERAL | Remove all references to City of Houston. | AGREE
GENERAL | Check north arrows on all sheets. | AGREE
GENERAL | Check match line sheet numbers on all sheets. | AGREE
GENERAL | Check for spelling & labeling errors throughout the set, some have been noted in markups, but not all. | AGREE
GENERAL | All airside plan sheets much be submitted to airport staff and Garver for review and approval also. | AGREE
GENERAL | You may want to wait to seal the plans until you receive approval and submit for stamping to reduce the need for revclouds and revision notes. | AGREE | REVCLOUDS HAVE BEEN ADDED
GENERAL | In the plan set, also include (or submit simultaneously) plans for the access road relocation, fuel farm entry relocation, & George Haddaway improvements. | DISAGREE | THESE IMPROVMENTS ARE BEING DESIGNED FOR THE AIRPORT BY GARVER, SO THEY ARE OUTSIDE THE SCOPE OF THIS PROJECT. THE FUEL FARM RELOCATION AND PERIMTER ROAD REPAIRS CAN BE FOUND IN THE PLAN SET BY GARVER DATED JUNE, 2019 (TOA PROJECT BID NO. 19-223). GEORGE HADDAWAY IMPROVEMENTS ARE BEING WORKED ON NOW, THEREFORE WE DO NOT KNOW THE PROJECT NUMBER.
GENERAL | Include plans with fire truck routing using autoturn (or similar) to show adequate turn radii & paths through the site. Use WB-50 vehicle for modeling. | AGREE | SEE SEPARATE TRUCK MANEUVERING EXHIBIT
GENERAL | Label the car wash on all applicable sheets. | AGREE
GENERAL | Will detention pond maintenance be accessed from airside or landside? | AGREE | PRIVATE POND-CLIENT WILL PERFORM THE NECESSARY MAINTENANCE
GENERAL | Reference markups for additional comments & detailed markups. | AGREE
C00.02 | Sheet C00.09 is listed in the sheet table but not included in the set | AGREE
C00.04 | Reference markups for revisions/additions to notes. | AGREE
C00.05 | Check survey control coordinates. Reference markups | AGREE
1 of 4 | Revise sheet number to match rest of set nomenclature | AGREE
1 of 4 | Update per zoning plan changes - should reflect approved zoning plan (have not received resubmittal for review & approval). | AGREE
1 of 4 & C05.03 | What is the paved area north of Hangar III and south of George Haddaway? Parking? Loading? Storage? | AGREE | STORAGE
C00.10 | Hydrants must maintain minimum 3' (prefer 6') clear from bldg foundation for future maintenance/service. | AGREE
C01.00 & 03.01 | Extend project limits to encompass ALL paving/grading/drainage/utility work. | DISAGREE | THIS LINE WAS ACTUALLY THE LEASE LIMITS, SEE UPDATED CALLOUTS
C01.01 | Does the existing double 24" RCP have SET's or headwalls? | AGREE | SET's
C01.02 & 01.03 | Check your viewports - plan view doesn't line up with labeling arrows. | AGREE
C02.01 & 02.02 | Include CI protection on Addison Rd inlets. | AGREE
C02.03 | Revise sheet number | AGREE
C02.03 | Use TOA standard details where applicable. | AGREE
C03.01 | Note to remove existing landscaping as applicable. | AGREE
C03.01 & 11.02 | Where is the OH being relocated? Show. | AGREE | SEE SHEET C18.01 FOR PROPOSED RELOCATION
C03.01 | Demo sidewalk to property line & connect back to ex. | AGREE
C03.02 | Coordinate fence/gate removal with airport to maintain security & fire access. | AGREE
C03.02 | Show ex. Sanitary service lines & cleanouts | DISAGREE | ALL KNOWN UTILITIES ARE SHOWN
C03.02 | Water should be cut & plugged at the cross. | AGREE
C03.03 & 03.04 | Connect ex. Water line crossing Addison Rd to proposed line, demo ex line beyond extension point. | DISAGREE | SEE WATERLINE PLANS FOR CONNECTION LOCATION
C03.04 | Show all existing drainage pipes across the site - coordinate with Dave Wilde to get records. | AGREE | ADDED THE DRAINGE COMING FROM THE FUEL FARM
C03.04 | Remove tee on northern end of demo'd water line | AGREE
C04.01 | Where is the new access road? Show location & connection to it. | DISAGREE | ACCESS ROAD PROVIDED BY OTHERS
C04.03 | Call for 1" expansion joint on details 3 & 5 | AGREE
C05.01 | Label all curb curve radii | AGREE
C05.01 | Add detail nomenclature to the legend (typ) | AGREE
C05.01 & 05.05 | Light duty pavement called out in the legend doesn't match the pavement detail. Should call for medium duty. (typ) | AGREE
C05.01 | Transition sidewalk to match existing at the southern property line. | DISAGREE | THE PROPOSED SIDEWALK IS TIEING INTO THE EXISTING CURB AT A 90. THIS WILL BE BEST FOR FURURE TIE IN, AS THERE WILL NOT BE ANY ADDITIONAL SIDEWALK REMOVAL NEEDED.
C05.01 | Should be 5" sidewalk. (typ) | AGREE
C05.02 | What is the darker cross-hatched area? It is not labeled or in the legend. If it is pedestrian accessible, it should have ramps. | DISAGREE | THAT AREA IS ONLY FOR LANDSCAPE NOT A SIDEWALK
C05.02 | Do you need a publicly accessible route from the street? | DISAGREE | THIS AREA IS LANDSCAPE
C05.02 & 09.02 | Is the stamped pavement at the main FBO entrance curbed? Are there curb transitions at the entrance to the covered drive? | AGREE | YES THE DRIVE AND SIDEWALK WILL BE STAMPED. THE CURB IS RAMPING UP FROM NORTH END AND RAMP DOWN ON THE SOUTH
C05.05 | Alley pavement details are not applicable to fire lanes. If you intended to use it for the inverted crown, please provide a detail that reflects TOA paving standards with your intended grading. | AGREE | SEE DETAIL 1 ON SHEET C05.05 FOR UPDATED CROSS SECTION
C05.05 & 05.06 | Get the updated BFR detail from Dave Wilde & replace. You don't need the detectable warning paver detail. | AGREE | SEE DETAIL 6 ON SHEET C05.05
C05.06 | Because Addison Rd is asphalt, provide a concrete-to-asphalt transition detail. | AGREE | SEE DETAIL 6 ON SHEET C05.06
C05.06 & 09.01 | Include a concrete curb & gutter on asphalt pavement detail. | AGREE
C06.02 | Check legend - looks like the isolation & expansion joints may be switched? (typ) | AGREE
C06.03 | Detail 8 should be expansion joint, not isolation joint - has a dowel. | AGREE
C07.01 & 07.02 | Dimension sawcut | AGREE
C07.01 & 07.02 | Call for concrete to asphalt transitions on both driveways. | AGREE
GRADING | Add elevations at existing pvmt connections to elevation point sheets | AGREE
GRADING | Please move the grading plan sheets to immediate follow the elevation point sheets. | AGREE
C09.01 | Provide grades for curb replacement | AGREE
C09.01 | BFR's should have return curbs, not wings. | AGREE
C09.01 | Add TOC & back of sidewalk grades w/ max 2% grade callouts for parkway. | AGREE
C09.02 | If the darker crosshatched area is pedestrian, need spot grades. | DISAGREE | THIS AREA IS FOR LANDSCAPE
C10.00 | Need pre-development & post-development DAM's. | AGREE | AN EXISTING DAM SHEET HAS BEEN ADDED
C10.00 & 12.07 | Seems that at least some of the fuel farm drainage is captured by or flows through your site. Coordinate with Dave Wilde for records & show how this is being handled. | AGREE | THE FUEL FARM DRAINAGE HAS BEEN INCORPORATED INTO THE SYSTEM
C10.00 | Legend shows DA boundaries are existing, but they match the proposed layout. | AGREE
C10.01 | City of Houston drainage manual??? | AGREE | ALL STORM CALCULATIONS ARE PERFORMED PER TOWN OF ADDISON DRAINAGE CRITERIA MANUAL, SEE UPDATED NOTE
C10.01 | Why are you using different intensities for the western & eastern collection lines? | DISAGREE | WESTERN ZONE IS CLOSED STORM SEWER SYSTEM, REQUIRING DESIGN STORM FREQUENCY OF 10YR WITHIN STORM SYSTEM. EASTERN ZONE IS CLOSED SYSTEM AT LOW POINT OR SAG, REQUIRING 100YR WITHIN STORM SYSTEM.
C10.01 | Both storm drain lines outfall at the detention pond, so should match beginning HGL's, which should match the 100-yr WSL of the pond. | AGREE | DOWNSTREAM HGL ELEVATIONS HAVE BEEN UPDATED FOR 100YR WSL OF POND
C10.01 | Need calcs for the 3'x6' RCB downstream of the pond also. | AGREE | SEE SHEET C11.03
C11.01 | Where is cross section 'A-A' as shown on sheet? | AGREE | SEE SHEET C10.08
C11.01 | Geometry of your proposed channel connection to the existing storm drain is awkward - revise to be cleaner. | AGREE
C11.02 | Show maintenance access for pond & check appropriate grading | DISAGREE | PRIVATE POND-CLIENT WILL PERFORM THE NECESSARY MAINTENANCE
DRAINAGE | Provide stage-storage calcs for the pond, including pre-/post runoff calcs. | AGREE | SEE SHEET C11.03
DRAINAGE | Don't see location of your outfall structure for the pond. Show location & orifice sizing for 100-yr storm and emergency overflow. Reference TOA drainage manual for requirements. | AGREE | SEE SHEET C11.03
DRAINAGE | No tee connections on storm drains, prefer wyes or junction boxes/manholes. | AGREE | TEE CONNECTIONS HAVE BEEN CONVERTED TO WYE'S AND MANHOLES
DRAINAGE | Label sizes of storm manholes & confirm wall integrity w/ larger pipe sizes & configurations. | AGREE
C12.01 | Is this a pilot channel? Clarify & label. | AGREE | THIS IS NOT A CONCRETE CHANNEL
C12.02 | Check invert elevations for trench drains and STM-16, does not seem to be positive drainage flow. | AGREE | INVERT ELEVATIONS HAVE BEEN CORRECTED
C12.04 | STM-4 calls for a pipe size change - is this for the 24" joining the main line? Clarify. | AGREE | THIS HAVE BEEN CHANGED TO A WYE CONNECTION
C12.08 | Refer to TOA Drainage Criteria Manual fore storm plan requirements. | AGREE
C12.08 | Show and label HGL100 | AGREE
C12.09 | Addison uses "flows to creek" storm drain covers. | AGREE
C12.09 | Reference NCTCOG for backfill standard specs | AGREE
C12.10 | Are the catch basins in the detail the aircraft rated inlets? Where are these being used? | AGREE | YES, THESE ARE AIRCRAFT-RATED
C12.11 | Do you want a cleanout on the roof drains? (not a requirement, just a question) | DISAGREE | REF MEP FOR ROOF DRAIN CLEANOUTS
SANITARY | Check clearances on all water/sewer crossings & ensure clearances or encasement per TCEQ requirements. Show & label any required encasement. | AGREE
SANITARY | Are there bathrooms/sinks/showers in the hangars? If so, how are they connecting to sanitary? Same service(s) as the floor drain(s) or separate connections? | AGREE | THERE ARE RESTROOMS IN HANAGR 1 AND 3 AS WELL IN THE FBO
SANITARY | Legend - why clamp? Also, symbol doesn't match what's shown on the plans, and if it's a different symbol, where is it being used? | AGREE | CHANGED TO MATCH
C13.01 | Is the sanitary service for Hangar 1 crossing the water services? It's not clear since bldg connection isn't shown. Would prefer that it not. | DISAGREE | THE SANITARY SERVICE IS NOT CROSSING.
C13.01 | Cleanouts at all bldg connections | DISAGREE | THE CLEANOUTS AT THE BUILDINGS ARE TO BE DETERMINED BY THE MEP
C13.02 | Would like SAN-16 MH moved into drive & outside of the landscape island | AGREE
C13.02 | Profile the dumpster service & show encasement where it crosses the water | AGREE
C13.02 | Show & profile the new service that will be required for the discharge from the fuel farm oil/water separator, encase it where it crosses the water. | AGREE | A SANITARY SEWER LINE HAS BEEN PROVIDED TO THE FUEL FARM LEASE LINE. GARVER TO DESIGN AND RELOCATE THE OIL/WATER SEPARATOR TO THE NEW SS LINE
C13.02 | 6" service connections require manholes @ main, not tees/wyes. | AGREE
C13.02 | Car wash drains should be connected to sanitary sewer (b/c of soap/detergents), & should have oil/water separator (check with TOA Environmental Services & plumbing codes to confirm). If allowed to discharge to storm, will need another stormwater interceptor on the eastern trunk line downstream of the car wash lateral. | AGREE
C13.02 | What is being dumped at the waste station at SAN-21? Does it need an oil/water separator also? | DISAGREE | THAT IS JUST A NORMAL SS WASTE, A OIL/WATER SEPARATOR IS NOT NEEDED
C13.02 | Put cleanouts at bends. | AGREE
C13.03 | On shallow clearances between SD & SS w/ SD on top of SS, would like to see some kind of encasement (conc or steel) for those sections to protect against the weight and any future settling of the SD and SD embedment. | AGREE | SEE NOTE 4 ON SANITARY SEWER PLAN SHEETS
C13.04 | TOA has new batch of MH covers that reflect the "new" logo note that these should be procured from public works. | DISAGREE | D.W. DID NOT HAVE THE UPDATED LOGO DESIGN ON A STANDARD DETAIL SHEET
WATER | Check clearances on all water/sewer crossings & ensure clearances or encasement per TCEQ requirements. Show & label any required encasement. | AGREE
WATER | Label which services are domestic/fire/irrigation. | AGREE
WATER | Add valves as noted in the markups & water system requirements (valve on each leg of a tee unless in close proximity to another valve on the same line - deletion of a valve is at staff discretion). | AGREE | ADDITIONAL VALVES HAVE BEEN PROVIDED, SEE WATERLINE PLAN SHEETS. VALVES NOT NECESSARY AT EACH LEG OF FHA TEES
WATER | Show all applicable vaults & BPA's (must be outside of vehicular surfaces) | AGREE
WATER | See additional notes on 14.01 & 14.02, which should be added to all water sheets. | AGREE
WATER | Check legend. Water valve symbols & corresponding symbols on the plan sheets - circle w/ strike seems to be for existing valves, and hourglass shape for proposed, but not noted that way in the legend. Water linetypes in the legend don't match what was used in the plans. | AGREE
WATER | Dimension water line separation from west side of hangars. Must have a minimum 7.5' clearance from foundations (building & ramps) for maintenance purposes. | AGREE
WATER | What are the circles at the end of the fire lines? Wall-mounted FDC's? Other? Clarify. | AGREE
WATER | Include station equations where applicable in labels (plan & profile). | AGREE
WATER | Call for guard posts around airside FHA's & include standard detail. | AGREE
WATER | 4" connections should be saddle & corp, not tee. | AGREE
C14.01 | Would like to see FHA @ 300+58 moved west & a tee added to get the distance. | DISAGREE | SEE THE CURRENT FIRE HYDRANT ASSEMBLY LOCATION ON SHEET C14.01.
C14.01 | Why is a 4" plug on a 2" service at 102+83? | AGREE
C14.01 & 14.02 | Existing Addison Rd crossing should be connected to the proposed 8" water line. See markups for further info on connection & demo. | AGREE | THE FIRE HYDRANT HAS BE RELOCATED AND A CONNECTION HAS BEEN ADDED
C14.02 | Check with Fire Marshall re: length of FDC from the hydrant at fire line STA 107+29 (if the circle @ end of line is an FDC). | AGREE
C14.02 | No water fittings within 10' of sanitary crossings. | AGREE
C14.02 | Ensure min. 10' separation (CL-CL) between water & sewer lines. | AGREE
C14.03 | On shallow clearances between SD & water w/ SD on top of water would like to see some kind of encasement (conc or steel) for those sections to protect against the weight and any future settling of the SD and SD embedment. | AGREE | SEE NOTE 5 ON WATERLINE PLAN SHEETS
C14.03 | Show all crossings, including service crossings, in the profiles. | AGREE
C14.03 | Show valves in profiles. | AGREE
C14.05 | Not using RCCP water main - don't include RCCP embedment detail - use PVC detail SD-W01. | AGREE
C15.00 | Dimension the separation from the water & gas (min. 4') | AGREE
C15.00 | Include profile for Addison Rd crossing. | DISAGREE | THE GAS CROSSING THE ROAD WILL BE DONE BY GAS PROVIDER
PVMT MARKING | Airside markings need to reflect access road changes. Coordinate with the airport & Garver. | AGREE
PVMT MARKING | Stripe applicable areas in front of/near FHA's on the airside for NO PARKING. Include detail (similar to sketch on C16.04) for striping & bollards/guard posts. | DISAGREE | THERE WILL BE NO VEHICLE PARKING ON AIRSIDE/APRON
C16.04 | Extend fire lane stripes all the way to access gate between Hangar I & FBO. | AGREE
C16.04 | The circle under the canopy on FBO is striped as fire lane. Interior radii aren't labeled anywhere for these curves - are they fire lane compliant? Does the circle need to be firelane? | AGREE | SEE UPDATED FIRE LANE WITH RADII DIMENSIONS
C16.05 | Does the paved area north of Hangar III and south of George Haddaway need fire lane striping for George Haddaway? | DISAGREE | NO, THIS AREA DOES NOT NEED FIRE LANE STRIPING
FENCING | Coordinate knox locations w/ Fire Marshall. Does there need to be Knox access on both sides of the gates that access public roads? | AGREE | KNOX LOCATIONS TO BE COORDINATED WITH FIRE MARSHALL
C17.02 | Will the proposed AOA gate to the fuel farm be swing or slide? | AGREE | GATE IS TO SLIDE, SEE UPDATED LABEL
C17.04 | Detail for swing gate? | AGREE | SEE SHEET C17.03
LANDSCAPE | Many proposed trees are too close to utility lines/appurtenances. Tree trunks should be a minimum of 8' from outside edge of utilities. | AGREE
LANDSCAPE | Show concrete pads for FHA's/Valves/MH's/vaults, etc. | AGREE
LP1.01 | Include transportation visibility triangles (Fig 3.6), not just the landscape triangles. | AGREE
LP1.01 | No seeding. Sod. | AGREE
LP1.01 | Include re-establishment of newly graded/re-graded areas south of site. | DISAGREE | SEE CIVIL PLANS FOR NEWLY GRADED/RE-GRADED AREAS TO THE SOUTH OF THE SITE.
LP1.02 | Discuss possibility of moving water line further west and trees further east (see markups) with civil eng in order to keep trees on either side of the fuel farm access. | AGREE
Notes: 1. | Response: Appropriate response is Agree (Correction Made) or Disagree (Correction Not Made), Explanation Required.
2. | This form must be completed and returned with future submittals.
3. | Previous red lined Plan Review Set must be submitted with future submittals.
4. | Failure to submit Completed Summary of Review Comments form and previous Plan Review Set
will result in a delay of future plan sets being reviewed.
5. | Send all plan submittals directly to the Town of Addison